## Lambda Heat Pump Sensors
Module Type | Sensor ID | Name | Description | Unit | Data Type | Read/Write | Min Value | Max Value | Scale | Precision | Modbus Address
General Ambient | amb_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 0000
General Ambient | amb_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 0001
General Ambient | amb_actual_ambient_temp | Actual Ambient Temperature | Current ambient temperature | °C | int16 | RW | -50 | 80 | 0.1 | 1 | 0002
General Ambient | amb_average_ambient_temp_1h | Average Ambient Temperature 1h | Average temperature of the last 60 minutes | °C | int16 | RO |  |  | 0.1 | 1 | 0003
General Ambient | amb_calculated_ambient_temp | Calculated Ambient Temperature | Calculated temperature for heat distribution modules | °C | int16 | RO |  |  | 0.1 | 1 | 0004
Heat Pump | hp_error_state | Error State | Current error state |  | uint16 | RO |  |  | 1 | 0 | 1000
Heat Pump | hp_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 1001
Heat Pump | hp_state | State | Current state |  | uint16 | RO |  |  | 1 | 0 | 1002
Heat Pump | hp_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 1003
Heat Pump | hp_flow_temp | Flow Temperature | Flow line temperature | °C | int16 | RO |  |  | 0.01 | 2 | 1004
Heat Pump | hp_return_temp | Return Temperature | Return line temperature | °C | int16 | RO |  |  | 0.01 | 2 | 1005
Heat Pump | hp_volume_flow_sink | Volume Flow Sink | Volume flow heat sink | l/min | int16 | RO |  |  | 0.01 | 2 | 1006
Heat Pump | hp_source_inlet_temp | Source Inlet Temperature | Energy source inlet temperature | °C | int16 | RO |  |  | 0.01 | 2 | 1007
Heat Pump | hp_source_outlet_temp | Source Outlet Temperature | Energy source outlet temperature | °C | int16 | RO |  |  | 0.01 | 2 | 1008
Heat Pump | hp_volume_flow_source | Volume Flow Source | Volume flow energy source | l/min | int16 | RO |  |  | 0.01 | 2 | 1009
Heat Pump | hp_compressor_rating | Compressor Rating | Compressor power rating | % | uint16 | RO |  |  | 0.01 | 2 | 1010
Heat Pump | hp_heating_power | Heating Power | Current heating power | kW | int16 | RO |  |  | 0.1 | 1 | 1011
Heat Pump | hp_power_consumption | Power Consumption | Frequency inverter power consumption | W | int16 | RO |  |  | 1 | 0 | 1012
Heat Pump | hp_cop | COP | Coefficient of Performance |  | int16 | RO |  |  | 0.01 | 2 | 1013
Heat Pump | hp_energy_consumption | Energy Consumption | Electric energy consumption since last reset | Wh | int32 | RO |  |  | 1 | 0 | 1020
Heat Pump | hp_energy_output | Energy Output | Thermal energy output since last reset | Wh | int32 | RO |  |  | 1 | 0 | 1022
Boiler | boil_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 2000
Boiler | boil_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 2001
Boiler | boil_actual_high_temp | Actual High Temperature | Current temperature upper sensor | °C | int16 | RO |  |  | 0.1 | 1 | 2002
Boiler | boil_actual_low_temp | Actual Low Temperature | Current temperature lower sensor | °C | int16 | RO |  |  | 0.1 | 1 | 2003
Boiler | boil_circulation_temp | Circulation Temperature | Current temperature circulation sensor | °C | int16 | RO |  |  | 0.1 | 1 | 2004
Boiler | boil_circulation_pump_state | Circulation Pump State | Current state of circulation pump |  | int16 | RO |  |  | 1 | 0 | 2005
Boiler | boil_max_boiler_temp | Maximum Boiler Temperature | Setting for maximum boiler temperature | °C | int16 | RW | 25 | 65 | 0.1 | 1 | 2050
Buffer | buff_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 3000
Buffer | buff_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 3001
Buffer | buff_actual_high_temp | Actual High Temperature | Current temperature upper sensor | °C | int16 | RO |  |  | 0.1 | 1 | 3002
Buffer | buff_actual_low_temp | Actual Low Temperature | Current temperature lower sensor | °C | int16 | RO |  |  | 0.1 | 1 | 3003
Buffer | buff_modbus_buffer_temp_high | High Temperature (Modbus) | Buffer temperature set via Modbus | °C | int16 | RW | 0 | 90 | 0.1 | 1 | 3004
Buffer | buff_request_type | Request Type | Type of current request |  | int16 | RW |  |  | 1 | 0 | 3005
Buffer | buff_request_flow_line_temp | Request Flow Line Temperature | Requested flow line temperature | °C | int16 | RW | 0 | 65 | 0.1 | 1 | 3006
Buffer | buff_request_return_line_temp | Request Return Line Temperature | Requested return line temperature | °C | int16 | RW | 0 | 60 | 0.1 | 1 | 3007
Buffer | buff_request_heat_sink_temp_diff | Request Heat Sink Temperature Difference | Requested temperature difference | K | int16 | RW | 0 | 35 | 0.1 | 1 | 3008
Buffer | buff_request_heating_capacity | Request Heating Capacity | Requested power | kW | int16 | RW | 0 | 25.5 | 0.1 | 1 | 3009
Buffer | buff_max_buffer_temp | Maximum Buffer Temperature | Setting for maximum buffer temperature | °C | int16 | RW | 25 | 65 | 0.1 | 1 | 3050
Solar | sol_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 4000
Solar | sol_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 4001
Solar | sol_collector_temp | Collector Temperature | Current temperature collector sensor | °C | int16 | RO |  |  | 0.1 | 1 | 4002
Solar | sol_buffer1_temp | Buffer 1 Temperature | Current temperature buffer 1 sensor | °C | int16 | RO |  |  | 0.1 | 1 | 4003
Solar | sol_buffer2_temp | Buffer 2 Temperature | Current temperature buffer 2 sensor | °C | int16 | RO |  |  | 0.1 | 1 | 4004
Solar | sol_max_buffer_temp | Maximum Buffer Temperature | Setting for maximum buffer temperature | °C | int16 | RW | 25 | 90 | 0.1 | 1 | 4050
Solar | sol_buffer_changeover_temp | Buffer Changeover Temperature | Setting for buffer changeover temperature | °C | int16 | RW | 25 | 90 | 0.1 | 1 | 4051
Heating Circuit | hc_error_number | Error Number | Error code |  | int16 | RO |  |  | 1 | 0 | 5000
Heating Circuit | hc_operating_state | Operating State | Current operating state |  | uint16 | RO |  |  | 1 | 0 | 5001
Heating Circuit | hc_flow_line_temp | Flow Line Temperature | Current temperature flow line sensor | °C | int16 | RO |  |  | 0.1 | 1 | 5002
Heating Circuit | hc_return_line_temp | Return Line Temperature | Current temperature return line sensor | °C | int16 | RO |  |  | 0.1 | 1 | 5003
Heating Circuit | hc_room_device_temp | Room Device Temperature | Current temperature room device sensor | °C | int16 | RW | -29.9 | 99.9 | 0.1 | 1 | 5004
Heating Circuit | hc_set_flow_line_temp | Set Flow Line Temperature | Target flow line temperature | °C | int16 | RW | 15 | 65 | 0.1 | 1 | 5005
Heating Circuit | hc_operating_mode | Operating Mode | Current mode of operation |  | int16 | RW |  |  | 1 | 0 | 5006
Heating Circuit | hc_target_flow_line_temp | Target Flow Line Temperature | Calculated target flow temperature | °C | int16 | RO |  |  | 0.1 | 1 | 5007
Heating Circuit | hc_set_flow_line_offset_temp | Set Flow Line Offset Temperature | Offset for flow temperature | °C | int16 | RW | -10 | 10 | 0.1 | 1 | 5050
Heating Circuit | hc_set_room_heating_temp | Set Room Heating Temperature | Setting for room temperature setpoint heating operation | °C | int16 | RW | 15 | 40 | 0.1 | 1 | 5051
Heating Circuit | hc_set_room_cooling_temp | Set Room Cooling Temperature | Setting for room temperature setpoint cooling operation | °C | int16 | RW | 15 | 40 | 0.1 | 1 | 5052